## Instructions for specs
Please read the instructions carefully to ensure that all required documentation is submitted.
Only complete bids with all tabs filled and supplemental documentation attached will be considered.
Tab: "1 - VIE Systems maintenance
This table contains the maintenance requirements for the VIE system included in the RFP.
The maintenance have to follow the tank and vaporiser manufacturer recommendations/requirements
Please review these requirements carefully before preparing the technical proposal.
Vendors must submit proposals indicating that these requirements are met.

## LOX Manufacturer
Component | Specification | Meets requirement? (Yes/No/NA) | Type of supporting document (select from drop down) | File name as submitted | Page No. | Comments
Volume | Minimum of 1.5 tonnes of LOX each month until December 2023
Regulatory | Proof of stringent regulatory authority (SRA) approval for medical LOX
OR
Proof of product meeting the requirements of an SRA pharmacopeia (e.g., USP, Ph Eu, BP, or IP) as shown by their specification and a sample Certificate of Analysis (CoA).
Good Manufacturing Practices(GMP) | Address of the manufacturing facility
Certificate of Analysis (CoA) template to indicate alignment with USP, Ph Eu, Int’l Pharmacopoeia, or British Pharmacopoeia
Copy of the manufacturer’s license to distribute medical oxygen or license as a wholesaler of medical oxygen
Proof of GMP OR the following:
• Certification of ASU, and storage tanks for oxygenservice for medical application.
• Cleaning protocols for tanks (storage and transport) (e.g., cleaned to ISO 23208 with ‘cleaned for O2’ indicated in scope).
• Audit history of a manufacturing facility from the past 3 years (including validity dates for audits).
• Facility safety directives.
• If a manufacturer is producing industrial and medical LOX, an explanation of when the product streams are separated and how contamination is prevented.
• Explanation of how a batch of medical LOX is defined.
• Validation of manufacturing and cleaning processes.
Quality Management Systems | ISO 9001: Quality Management Systems - Requirements
Documentation | Evidence of sale of medical LOX to government body
Evidence of Long-Term Agreement with global procurement bodies (if available)

## LOX transport
Component | Specification | Meets requirement? (Yes/No/NA) | Type of supporting document (select from drop down) | File name as submitted | Page No. | Comments
Volume | Minimum of 1.5 tonnes of LOX each month until December 2023
Good Manufacturing Practices(GMP) | Address of the transportation company headquarters
Copy of the transporter/supplier’s license to distribute medical oxygen or license as a wholesaler of medical oxygen
Copy of export license for the transport of medical oxygen if border crossing
Certification of liquid transport vehicles for oxygen service for medical application.
Cleaning protocols for transportable cryogenic vessels (e.g., cleaned to ISO 23208 with ‘cleaned for O2’ indicated in scope).
Safety directives or procedures related to ensuring safe trasnport of medical LOX
If transporter distributes industrial and medical LOX, explanation of how contamination of transport vessels is prevented
Explanation of how a batch of medical LOX is defined.
Validation of cleaning processes.
Evidence of maintaining pressure differential between tanker truck and bulk storage tank during filling to prevent backflow.
A letter of authorization from the company making the deliveries to the company supplying the LOX (if applicable).
Quality Management Systems | ISO 9001: Quality Management Systems - Requirements
Documentation | Evidence of sale of medical LOX to government body
Evidence of Long-Term Agreement with global procurement bodies (if available)

## VIE Systems maintenance
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | The maintenance activities shall be performed on the VIE system comprising a bulk LOX storage tank, an ambient vaporizer, and pressure controls installed at Limbe Regional Hospital, Limbe, Cameroon (4.02239, 9.20917) Activities to include:
Carrying out necessary maintenance at pre-determined intervals.
Carrying out any repair work deemed necessary.
Conducting continued knowledge transfer to facility operations staff on mechanisms of operations
Ensuring that standard daily checks performed by facility staff are conducted and recorded appropriately.
Producing service report for every intervention.
Provision of parts during the duration of the contract ( 2 years )
Operational and safety Requirements | Maintenance operations shall only be carried out by personnel qualified for the task, using manufacturer’s instructions
Maintenance shall be carried out under a "Permit to work", issued by the facility representative for quality systems, to ensure minimization of disruption to facility operations and workflows.
The maintenance and assembly of equipment for oxygen shall be carried out under clean, oil free conditions
Degrease all new parts (spare parts) with a recommended degreasing agent.
Ensure no smoking, hot work, open flames in the surrounding area unless suitable precautions are taken (e.g. if hot-work such as welding is deemed necessary).
Replacement parts should be from the original equipment manufacturer or their recommended equivalents.
All modifications in design, materials or equipment (parts) and repairs shall be approved by an authorised representative or the manufacturer. If modifications are to tank, these shall be inspected upon completion, certified, and documented in tank databook.
Verify that placement of system component labels and safety warning signage (Restricted access, no parking, safety, no smoking, maintenance in process) remain in accord with industry norms.
Maintenance checks | Leaking valves - If connections are observed as loose, they should be carefully tightened. If this does not resolve the issue, - connections should be depressurized before rectification if possible. If neither of the above are possible, there will be oxygen enrichment around the system until the tank empties. Extreme caution should be taken with any movement/works in the surrounding vacinity.
De-icing different frozen parts of the systems ( Direct flame or intense heat shall never be used )
Assessment of the vacuum between the inner vessel and the outer jacket (annular space) when indicated
Assessment of any changes of the operational conditions of the installation and its direct surroundings.
Checking the condition of the vessel, piping and accessories - that all remain intact with no visible signs of deterioration
Perform the operability and zero point check for pressure indicators.
Perform the operability check of valves.
Check status/integrity of safety valves
Zero point check of fluid level indicator
Check overfill protection system
Changing nearly or worn out parts ( eg. Seals etc..)
Check parts and connections ( flanges, couplings, pipe connections etc.); tighten any loose parts and components
Cleaning external parts
Documentations | Certification to carry out cryogenic sytem maintenance, evidence of experience with [brand] tanks.
Safety processes and quality control procedures to be followed
CVs of Lead Engineer and maintenance team.
Proposed work plan for maintenance intervals: activities, frequency.
References and Projects contracted in Cameroon (3 of each, from current year or within the past 3 years)
Product Performance Standards (or equivalent) | EN 12300 Cryogenic vessels - Cleanliness for cryogenic service
ISO 21009-2: Cryogenic Vessels - Static Vacuum Insultated Vessels Part 2: Operational Requirements
EN ISO 21009-2 Part 3: periodic inspections and all the other operational requirements.
EIGA DOC 224/20: Static Vacuum Insulated Cryogenic Vessels Operation and Inspection

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X