## Instructions for Specs
Reference number |  | ITB/CHAI/VIE/GHA_PH/0123
Please read the instructions carefully to ensure that all required documentation is submitted.
Only complete bids with all tabs filled and supplemental documentation attached will be considered.
Tab: "Tanks (General)"
This table contains general specifications for the bulk storage tanks included in the RFP.
Fill column C to indicate whether the product complies with the specification.
Fill column D to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column E with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: "Tanks (Product Specific)"
This table product contains specifications for bulk storage tank product line submitted by vendor in RFP.
Vendors must fill rows 3-8 for product line included in proposal
Tab: "Vaporizers (General)"
This table contains general specifications for ambient/passive vaporizers included in the RFP.
Fill column C to indicate whether the product complies with the specification.
Fill column D to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column E with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: "Vaporizers (Product Specific)"
This table product contains specifications for ambient/passive vaporizer product line submitted by vendor in RFP.
Vendors must fill rows 3-7 for product line included in proposal.
Tab: "VIE Civils"
This table contains general specifications for VIE civils works included in the RFP.
Fill column C to indicate whether the product complies with the specification.
Fill column D to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column E with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: - VIE Systems installation and commissioning
This table contains the installation and commissioning requirements for the VIE system included in the RFP.
The installation and commisionning have to follow the tank and vaporiser manufacturer recommendations/requirements
The installation and commisionning will be subjected to a third party authorized inspection agency ( AIA )
Please review these requirements carefully before preparing the technical proposal.
Vendors must submit proposals indicating that these requirements are met.
Tab: - First fill LOX Manufacturer"
This table contains the specifications for the filling of the VIE tank ( First fill) .
Please fill columns D, E, F, G, H as you prepare documents for your proposal and fill out the subsequent tabs of this spreadsheet.
Vendors must submit proposals indicating that these requirements are met.
Tab: - First fill LOX transport"
This table contains the specifications for tranporting the LOX for filling the tank ( First fill)
Please fill columns D, E, F, G, H as you prepare documents for your proposal and fill out the subsequent tabs of this spreadsheet.
Vendors must submit proposals indicating that these requirements are met.
Query period:
| Query email address: | GhanaUNITAIDOxygenProcurement@clintonhealthaccess.org

## 1a) Tanks-General
Reference number |  |  | ITB/CHAI/VIE/GHA_PH/0123
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Design Parameters | Vertical construction, stationary tank type
• Stainless steel or carbon steel outer shell
□ Affixed lifting lugs for use w/ clevis pins
• Stainless steel inner vessel (no aluminum)
• Stainless steel piping
• Vacuum pressure 0.05 bar (or better)
Maximum design pressure / test pressure (MAWP): 18 bar
Minimum / maximum operating temperatures:
• Inner vessel: -196°C /+20°C
• Outer shell: -30 °C /+50 °C
Sizing | See Tab "Tanks (Product Specific)"
Features | Operating:
• Fill coupling / type for LOX (spec type available)
□ Bottom and top-fill lines
• Pressure regulation
□ Pressure build-up/blow-down assembly
□ Pressure regulator with set-point feature for MAOP
• Overfill protection system, comprising
□ Fill line drain valve
□ Trycock vent valve
Monitoring:
• Liquid level gauge (& type to be specified)
• Liquid level transmitter (& type to be specified)
Safety:
•Thermal relief valve
• Safety valves: primary (set at MAOP) and secondary (set at MAWP) (no bursting discs)
Offtake (as a minimum):
• Primary discharge line for liquid offtake (specify availability of flange types)
• Economizer circuit
Documentation to be submitted with bid | Detailed description of any relevant experience of importing/suppling liquid medical oxygen storage tanks
Evidence of effectively managed after sales service, including but not limited to repair, warranties honored, and provision of spare parts
P&ID (reflective of requested features)
Sample databook, illustrative of what would be included (not limited to):
• Manufacturer's declaration of conformity
• 3rd party (e.g., Notified Body for PED) certificate of conformity and test reports, certificates for safety valves
• Commissioning, operations, and maintenance manual
• Detailed stress / loading calculations
Technical documentation of offloading requirements from transporting container
LOA between tank manufacturer and supplier (if applicable)
Warranty | 3 years minimum
The supplier must ensure the availability of spare parts for at least 8 years
Regulatory | PED 2014/68 EU (indicate NB) Or ASME “U” stamp
QMS | ISO 9001: Quality Management Systems - Requirements
Civils | See tab 3
Installation, testing, and comissioning | See tab 4
General design guidance (or equivalent) | EN 13458-1: Cryogenic vessels - Static vacuum insulated vessels - Part 1: Fundamental requirements
Process or component specific standards (or equivalent) | EIGA 200/17: The Safe Design, Manufacture, Installation, Operation and Maintenance of Valves Used in Liquid Oxygen and Cold Gaseous Oxygen Systems
ISO 8501-1: Preparation of steel substrates before application of pains and related products – visual assessment of surface cleanliness – Part 1: Rust grades and preparation grades of uncoated steel substrates and of steel substrates after overall removal of previous coatings
ISO 8504-2: Preparation of steel substrates before application of paints and related products – surface preparation methods – part 2: abrasive blast-cleaning
ISO 12944-4: Paints and varnishes – corrosion protection of steel structures by protective paint systems – Part 4: Types of surface and surface preparation
ISO 12944-5: Paints and varnishes – corrosion protection of steel structures by protective paint systems – Part 5: Protective paint systems
ISO 21009-2: Cryogenic vessels – Static vacuum insulated vessels – Part 2: Operational requirements
ISO 23208: Cryogenic vessels – cleanliness for service (specify for LOX service)

## 1b) Tanks- Product Specific
Product availability & associated specifications
Size, Tonnes LOX capacity | 5
Equivalent size, litres
Boil-off rate (indicate conditions)
Discharge capacity
Thermal conductivity
Insulation/fill material
Structural testing: wind & snow loading, earthquake rating

## 2a) Vaporizers- General
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Design Parameters | Ambient/passive vaporizer
• All aluminum
• Rated working pressure: ≥ 36 bar
• Design /maximum allowable working temp -196°C /+50°C
Inlet and outlet flange availability: ASME B16.5, BS PR C1, EN 1092, M40x2 thread, DIN 2635
All models designed according to PED 2014/68/EU, ASME SEC.VIII DIV.I, or ANSI B31.3
Sizing | See Tab "Vaporizers (Product Specific)"
Documentation to be submitted with bid | Detailed description of any relevant experience of importing/suppling passive/ambient vaporizers for medical LOX application
Evidence of effectively managed after sales service, including but not limited to repair, warranties honored, and provision of spare parts
LOA between ambient vaporizer manufacturer and supplier (if applicable)
Warranty | 2 year minimum
The supplier must ensure the availability of spare parts for the duration of the warranty and indicate lead times
Regulatory | PED 2014/68 EU (indicate NB) Or ASME “U” stamp
QMS | ISO 9001: Quality Management Systems - Requirements

## 2b)Vaporizers- Product Specific
Product availability & associated specifications
Nominal capacity (m3/hr) | 50
Equivalent size
Internal volume
Unit weight (dry)
Fin # / fin dimension
Structural testing: wind & snow loading, earthquake rating

## 3) VIE Civils
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | Civils shall be performed at the designated sites for VIE installation proposed by the vendor following site assessment
Activities shall include:
• Civil design for slab to bear load of filled 5-tonne tank, ambient vaporizer, and pressure regulating system to be tied in to medical gas pipeline system, inclusive of geotechnical requirements
• Site preparation
• Excavation
• Construction of reinforced slab for VIE system
• Engineering supervision during execution of civils
• Third party inspection by Authorized Inspection Authority (AIA), installation, testing, and commissioning
Security features, including but not limited to:
• Diamond wire chain-linked fence with height of at least 1.8m
• Lockable access gates
• Signage (Restricted access, no parking, safety, no smoking)
Installation, testing, and commissioning | During installation: Liase with CHAI technical consultant and MOH engineer(s) to make sure they are on site to oversee civil works as per design based on site/system-specific configurations prior to AIA.
Post work, provision of:
· Third party inspection report for VIE civils, inclusive of any testing
· Red-line original drawings of any agreed changes
Documentation to be submitted with bid | Detailed civil design DWG based on equipment configuration, load bearing requirements, and soil conditions at the site.
Geotechnical Study and/or soil testing report to inform the construction of a durable concrete platform to support the Liquid Oxygen tank at the site
Proposed Bill of Quantities aligned with civil design DWG
Detailed relevant work history including evidence of at least 3 years experience in designing and executing LOX-related civil design projects
Documentation of personnel training/qualifications, which may include: - CVs of Lead Civil Design Engineer and other key personnel necessary for project delivery - Certifications of personnel carrying out civils project - Summary of training program supplier requires of technical team involved in LOX-related civils projects
Safety and Quality Assurance Plans
Proposed work plan
3 References for VIE civils projects contracted within the past 3 years
Product Performance Standards (or equivalent) | SANS 2001-CC1 Construction works Part CC1: Concrete works (structural)
SANS 1200 DA Standardized specification for civil engineering construction Section DA: Earthworks (small works)

## 4) VIE install & commissioning
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | The installation, testing, and commisioning shall be performed at the designated site at the Police Hospital
Activities shall include:
• Installation, testing, and commissioning of VIE system inclusive of 5-tonne tank, ambient vaporizer, pressure regulating system, and tie-in to medical gas pipeline system
• Provision of mLOX first fill for system testing and commissioning (see tab 5 first fill LOX manufacturer and tab 6 first fill LOX transport)
• Third party inspection of installation by Authorized Inspection Authority (AIA) or equivalent.
Technical Requirements | The installation and commisioning shall be carried out per manufacturer and site-specific requirements
VIE tank must be unloaded by crane(s) capable of withstanding an approximate 5,000 kg load (to be confirmed) and to enable smooth and safe offloading
The VIE systems components shall be affixed to reinforced concrete structure with appropriately sized anchor bolts per manufacturer specifications, loading requirements, and stability analysis.
Tie-in of each VIE system to the medical gas pipeline systems of the Hospital
• Gas lines: Medical grade copper pipes, fittings, and accessories
• Liquid lines: stainless steel and are rated for oxygen and cryogenic service
Placement of system component labels and safety warning signage (Restricted access, no parking, safety, no smoking)
Installation, testing, and commissioning | During installation: Liase with MOH engineer(s) to make sure they are on site to oversee VIE installation as per manufacturer and site/system-specific configurations prior to AIA.
On-site: Inspection by authorized inspection authority (AIA), testing and commissioning shall be done before handover.
Provision of:
· Third party inspection report for installation, inclusive of any testing
· Testing report, to be written at time of first-fill, upon commissioning
· Commissioning report & certificate
Warranty | All components should have at least 2 years’ warranty period after commissioning
The supplier must ensure the availability of spare parts for at least 8 years
Within the warranty period, the supplier shall indicate response time to critical errors / incidents
Documentation | Site assessment plan including a checklist of requirements to be confirmed during pre-installation visit
Detailed relevant work history including evidence of at least 3 years experience in VIE system installations
Documentation of personnel training/qualifications, which may include: - CVs of Lead Engineer and installation team - Certifications of personnel carrying out installation - Summary of training program supplier requires of technical team involved in VIE system installations
Safety and Quality Assurance Plan
Proposed work plan
3 References for VIE system installation, testing and commissioning projects within the past 3 years
Product Performance Standards (or equivalent) | ISO 21009-2: Cryogenic Vessels - Static Vacuum Insultated Vessels Part 2: Operational Requirements
EIGA DOC 224/20: Static Vacuum Insulated Cryogenic Vessels Operation and Inspection

## 5) First fill LOX manufacturer
Component | Specification | Meets requirement? (Yes/No/NA) | Type of supporting document (select from drop down) | File name as submitted | Page No. | Comments
Volume | 5 tonnes
Regulatory | Proof of stringent regulatory authority (SRA) approval for medical LOX.
OR
Proof of product meeting the requirements of an SRA pharmacopeia (e.g., USP, Ph Eu, BP, or IP) as shown by their specification and a sample Certificate of Analysis (CoA).
Good Manufacturing Practices(GMP) | Address of the manufacturing facility used for the first fill during commissioning
Certificate of Analysis (CoA) template to indicate alignment with USP, Ph Eu, Int’l Pharmacopoeia, or British Pharmacopoeia
Copy of the manufacturer’s license to distribute medical oxygen or license as a wholesaler of medical oxygen
Proof of GMP OR the following:
• Certification of ASU, and storage tanks for oxygen service for medical application.
• Cleaning protocols for tanks (storage and transport) (e.g., cleaned to ISO 23208 with ‘cleaned for O2’ indicated in scope).
• Audit history of a manufacturing facility from the past 3 years (including validity dates for audits).
• Facility safety directives.
• If a manufacturer is producing industrial and medical LOX, an explanation of when the product streams are separated and how contamination is prevented.
• Explanation of how a batch of medical LOX is defined.
• Validation of manufacturing and cleaning processes.
Please provide a letter of authorization from between mLOX manufacturer and LOX infrastructure supplier if mLOX supply is outsourced.
Quality Management Systems | ISO 9001: Quality Management Systems - Requirements
Documentation | Evidence of sale of medical LOX to government body
Letter of authorization from between mLOX manufacturer and LOX infrastructure supplier if mLOX supply is outsourced.
Please list up to 5 institutional clients (e.g. international NGOs, large corporate bodies, government procurement agencies). Please include pertinent information about the relationship (e.g contract size, duration, products, etc.).

## 6) First fill LOX transport
Component | Specification | Meets requirement? (Yes/No/NA) | Type of supporting document (select from drop down) | File name as submitted | Page No. | Comments
Volume | Single delivery of 5 tonnes of mLOX to Police Hospital.
Good Manufacturing Practices(GMP) | Address of the transportation company headquarters and any relevant subsidiary for a company that will transport mLOX and carry out first fill procedures.
Copy of the transporter/supplier’s license to distribute medical oxygen or license as a wholesaler of medical oxygen
Copy of export license for the transport of medical oxygen if border crossing
Evidence of relevant certifications (e.g., TPED 2010/35/EU or US DOT) and labeling (e.g., GHS, DOT hazard class, UN ID 1073 class) of road tanker for oxygen service for medical application).
Cleaning protocols for transportable cryogenic vessels (e.g., cleaned to ISO 23208 with ‘cleaned for O2’ indicated in scope).
Safety directives, procedures, or internationally recognized guidelines (e.g., EIGA) that are followed to ensure safe transport and transfilling of medical LOX
If transporter distributes industrial and medical LOX, explanation of how contamination of transport vessels is prevented
Explanation of how a batch of medical LOX is defined.
Validation of cleaning processes.
Evidence of 'first fill’ procedures that will be followed during final testing and commissioning to transfill medical LOX from a road tanker to a newly installed empty bulk storage tank.
Evidence of maintaining pressure differential between tanker truck and bulk storage tank during filling to prevent backflow.
A letter of authorization from the company making the deliveries to the company supplying the LOX (if applicable).
Quality Management Systems | ISO 9001: Quality Management Systems - Requirements
Documentation | Evidence of sale of medical LOX to government body
Please list up to 5 institutional clients (e.g. international NGOs, large corporate bodies, government procurement agencies). Please include pertinent information about the relationship (e.g contract size, duration, products, etc.)

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X