## Medical air system
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Technical | Configuration:
• Triplex compressor
• Duty and standby dryer
Control panel:
• Digital display
• Continuous operations
• Clearly visible in English and/or preferred language of destination country, for at least:
§ Output pressure
§ System status, including current maintenance need
§ Cumulative hours of operation (digital or analogue meter)
Air compressor (includes motor and sub-assembly):
• Provides 100% system design flows with one compressor out of service
• Feed air compressor, either oil-free or filtered oil-injected or oil-lubricated rotary screw-type, minimum 750 kPa [108 psi]
• Noise: ≤ 67 dBA (Noiseless system)
Dryer, filter, and regulation system:
• Dessicant type dryer
• Sized for 100% of system peak calculated demand
• Pressure Dewpoint: -40 deg Celsius (- 40 F)
• Discharge pressure range: 345 kPa to 380 KPa [50-55 PSIG]
• Includes dew point meter
• Filter assembly to include dust filter (1 micron), duplex activated carbon filters, and duplex bacterial filter (0.01 micron)
Air receiver tank:
• Automatic drain
Power requirements
Compressor: 380V - 440V/50Hz (3 phase)
Infrastructure requirements | Supplier must indicate the following aspects to match infrastructure capabilities within facility:
• Acceptable mains capacity,
• Appropriate connection/adaptors,
• Compatibility with back-up power supply
• Infrastructure requirements for operation
• Appropriate housing including roofing, ventilation, air conditioning (if necessary), a clean room without oil, grease and petroleum-based or other flammable products.
Environmental Considerations | Operating temperature and humidity: 10–40 °C, 15-95% RH
Suitable to function at elevation 1,243m (4,078 ft) for Mbabane Government Hospital, whiles that of Piggs peak Governement Hospital is 1000m (3281ft).
Documentation | Provision of hard and soft copies of the following documents:
• Certificate of quality, calibration, and inspection
• User manual, detailing:
§ Protocols for operations
§ List of procedures and equipment required for cleaning
§ List of procedures and equipment for preventive maintenance
§ Troubleshooting chart
• Contact details of manufacturer, and authorized distributors (if applicable), and local service agents
• Product and model reference (brochure)
Installation, testing, and commissioning | Pre-shipment: Certificate of quality, calibration, and inspection
On-site:
• Installation to include training on start-up, use, and maintenance
• Inspection, testing and commission should be done before handover.
Verification to include:
• Pressure levels
• Electrical system functionality, alarms functionality
Conformity of installation shall be verified by a certified third party (if possible). Otherwise, alternative verification process to be agreed upon between vendor and owner.
Warranty | 2 years
Regulatory | Meets NFPA 99 or HTM 02-01 requirements for product output stream
QMS | ISO 9001: Quality Management Systems - Requirements
General design guidance (or equivalent) | Design, installation, testing, and commissioning of medical air system should be carried out as per:
• HTM-02-01: United Kingdom Department of Health: Health Technical Memorandum 02-01: Medical Gas Pipeline Systems -Part A Design, Installation, Validation and Verification
Or
• NFPA 99: National Fire Protection Association (USA): Health Care Facilities Code Handbook
Component specific performance standards (or equivalent) | ISO 8573-1: Compressed air – Part 1: Contaminants and purity classes.
ISO 8573-2: Compressed air – contaminant measurement – Part 2: Oil aerosol content.
ISO 8573-4: Compressed air – contaminant measurement – Part 4: particle content.
ISO 7396-1: Medical gas pipeline systems
All pressurized vessels to be:
• designed according to PED or ASME VIII, or equivalent.
• certified PED or ASME III, or equivalent.
• cleaned according to ISO 15001 ASTM G93, or equivalent.
Service level agreement | 60 months
Provide:
• Training schedule
• Training content
• Schedules for planned preventive maintenance (PPM)
• Define corrective maintenance, including repair agreements, delineating what falls out of warranty
• Provide time for response
• Provide time for availability of critical spares
Origin and/or warehouse location of spares

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X